## Summary
Equipment | Type | Location | Controller | Total Items | Passed | Failed | In Progress | Not Started | Completion %
AHU-1 | AHU | Main 1 Mechanical | MPC-1 | 6 | 0 | 0 | 0 | 6 | 0

## AHU-1
Item ID | Equipment | Point | Test Type | Description | Expected Result | Acceptance Criteria | Tools Required | Reference Doc | Status | Observed Result | Technician | Timestamp | Evidence | Notes
AHU-1-AHU-1 SAT-VIS-001 | AHU-1 | AHU-1 SAT | visual | Visual inspection of AHU-1 SAT wiring, termination, and labeling | Wiring matches drawings, labels present and legible, no damage | All terminations secure, wire labels match point list, no corrosion | Flashlight, Label maker (verify) | Point List: Row 1 | not_started
AHU-1-AHU-1 SAT-CON-001 | AHU-1 | AHU-1 SAT | continuity | Continuity test for AHU-1 SAT from controller to field device | Continuity confirmed, resistance within spec | < 1 ohm for digital, < 10 ohm for analog (per spec) | Multimeter, Test leads | Point List: Row 1 | not_started
AHU-1-AHU-1 SAT-CAL-001 | AHU-1 | AHU-1 SAT | calibration | Calibration verification of AHU-1 SAT against reference standard | Reading within ±±0.5°F (±0.3°C) of reference | Error ≤ ±0.5°F (±0.3°C) of span | Calibrated reference instrument, Multimeter, Calibration adapter | Point List: Row 1 | not_started
AHU-1-AHU-1 SAT-TRE-001 | AHU-1 | AHU-1 SAT | trend | Trend log verification for AHU-1 SAT | Trend configured, logging at correct interval, data retrievable | Interval matches spec, duration ≥ 30 days, no gaps | Controller workstation, Trend viewer | Point List: Row 1 | not_started
AHU-1-POWER-001 | AHU-1 | N/A (Equipment Power) | visual | Verify equipment power supply, disconnects, and overcurrent protection | Voltage within ±10% of nameplate, breakers sized correctly | Measured voltage matches nameplate ±10%, OCPD per NEC | Multimeter, Clamp meter |  | not_started
AHU-1-COMM-001 | AHU-1 | N/A (Controller Comm) | functional | Verify controller MPC-1 communication and time sync | Controller online, time synced, no comm errors | Heartbeat present, time within 1 sec of NTP, no error logs | Controller workstation, Network ping tool |  | not_started